Section 23 31 00

# PART-1	KITCHEN HOOD EXHAUST

1:1	SCOPE

- Provide factory built grease duct that is tested and listed by the Underwriters’ Laboratories, Inc. (UL 1978) for use with commercial cooking equipment, as described in NFPA-96.

- The U.L. listed insulated grease duct shall be certified for zero clearance to combustible material per UL 2221 with a 2 hour fire rating and have a 1 hour fire rating per ASTM-E2336.  Hourly ratings are met with use of factory fire stop at necessary floor/wall penetrations.

1:2	  CONSTRUCTION

- The double wall exhaust system shall have a 304 stainless steel inner liner (20 ga minimum) and an aluminized steel outer jacket (24 ga minimum). The materials and construction of the modular sections and accessories shall be as specified by the terms of the product’s U.L. listing.

- 10 pound ceramic fiber insulation between the inner liner and outer jacket shall be a nominal three inches thick.

- Aluminized steel surfaces exposed to the elements shall be protected by a minimum of one base coat of primer and one finish coat of corrosion resistant paint suitable for outer jacket skin temperatures of the given application. All primer and paint to be supplied by the installing contractor and shall be equivalent to series V2100 as manufactured by Rust-Oleum. Alternatively, an outer jacket constructed of 304 or 316 stainless steel may also be considered in lieu of painting.

- This exhaust system shall be designed and installed to be liquid tight and thus prevent leakage of grease and/or grease laden vapors into a building.

- Inner pipe joints shall be securely connected and sealed with factory supplied over-lapping V-bands and appropriate sealant as specified in the manufacturer’s installation instructions.

- Each system shall be designed to provide access for inspection and cleaning of each change of duct direction, permit drainage of grease residue through a duct section, enable the system to allow for the thermal expansion and allow various types of fire suppression equipment to be integrated into the grease ductwork, as necessary per local code.

# PART-2	EXECUTION

2:1	INSTALLATION

- Inner pipe joints shall be sealed by use of factory supplied overlapping V bands and sealant as specified in the manufacturer’s installation instructions.

- Roof penetrations shall be suitable for a noncombustible roof and shall be according to the manufacturer’s detail drawings and installation instructions.

- When installed according to the manufacturer’s installation instructions, the exhaust piping and its supporting system shall resist side loads at least 1.5 times greater than the weight per foot of the piping for both horizontal and vertical portions of the system.

- The exhaust system shall be installed according to the manufacturer’s installation instructions and shall conform to all applicable state and local codes.

- Provide all supports, guides, expansion joints, guy sections, guy tensioners, roof thimbles, roof flashings, storm collars and flip top terminations as required to provide a complete system per the manufacturer’s installation instructions.

- The entire exhaust system from hood to the termination point, including all accessories, except as noted, shall be from one manufacturer.

# PART-3	WARRANTY

3:1   WARRANTY

- The exhaust system shall have a limited lifetime warranty against functional failure due to defects in material and manufacturer’s workmanship from the date of installation.

- The manufacturer shall provide “to scale” drawings depicting the actual layout. The exhaust system shall be installed as designed by the manufacturer and in accordance with the terms of the manufacturer’s warranty and in conjunction with sound engineering practices.

- The factory built modular exhaust system shall be furnished by a vendor organization that assures design, installation and services coordination. As well as, providing “in-warranty” and “post-warranty” unified responsibility for owner, architect, consulting engineer and contractor.

# PART-4	PRODUCTS

  - MANUFACTURERS

- Product specification requirements shall be met by using Selkirk Commercial/Industrial Model IPS ZeroClear exhaust flue or equivalent as approved by the engineer. Equivalent submittals shall specify manufacturer’s model number, and other pertinent identification, and attest that the alternate material is in compliance with all specification requirements.

END OF SECTION 23 31 00