Section 23 51 00 or 23 35 00

# PART-1	ENGINE/GEN-SET & TURBINE EXHAUST PIPE

1:1	SCOPE

- Provide factory-built exhaust system that is tested, listed and labeled by the Underwriters’ Laboratories, Inc. for use with burning gas or liquid as described in NFPA-37 and NFPA-211, which produce exhaust flue gas temperatures not exceeding 1400oF under continuous operating conditions.  Additionally, the vent system shall be UL 103 & UL 2561 positive pressure tested and listed to 60 inches internal water column pressure.

1:2	  CONSTRUCTION

- The double wall exhaust system shall have a 304 (or 316) stainless steel inner liner (20 gauge min) and an aluminized steel outer jacket (24 gauge min). The materials and construction of the modular sections and accessories shall be as specified by the terms of the product’s U.L. listing.

The annular space between the inner wall and outer wall shall be:

- Nominal 1” thick of high temperature, body soluble fiber insulation or

- Nominal 2” thick of high temperature, body soluble fiber insulation or

- Nominal 4” thick of high temperature, body soluble fiber insulation

- Aluminized steel surfaces exposed to the elements shall be field-painted by a minimum of one base coat of primer and one finish coat of corrosion resistant paint suitable for outer jacket skin temperatures of the given application as published by the flue pipe manufacture. Alternatively, an outer jacket constructed of 304 or 316 stainless steel (24 gauge min) may also be considered in lieu of painting.

- This exhaust system shall be designed and installed to be gas tight and thus prevent leakage of combustion products into a building.

- Common pipe sections & fittings (ie; lengths/elbows/tees) shall have a self-centering sleeve to ensure proper alignment at the inner wall joint connection.

- Inner pipe joints shall be securely connected and sealed with factory supplied over-lapping V-bands and appropriate sealant as specified in the manufacturer’s installation instructions. Double wall outer joints, exposed to weather, shall also be caulked per the installation instructions.

- Connections to silencers and expansion joints shall be made with matching flanges.

- The exhaust system shall be designed and supported to compensate for all flue gas induced thermal expansion.

# PART-2	EXECUTION

2:1	INSTALLATION

- The prefabricated exhaust system shall be installed according to the manufacturer’s installation instructions, clearances to combustibles, factory submittal drawing, and shall conform to all applicable state and local codes.

- Provide all modular straight sections, fittings, supports, guides, relief valves, expansion bellows joints, roof thimbles, roof flashings, and terminations as required to provide a complete system per the manufacturer’s recommended design and installation instructions.

- The entire flue system from the silencer (if applicable) to the termination point, including all accessories, except as noted, shall be from one manufacturer.

- The termination shall comply to local code termination requirements and NFPA 37.

- Roof penetrations shall be suitable for the specified roof construction and shall comply with the manufacturer’s installation instructions.

# PART-3	WARRANTY

3:1   WARRANTY

- The prefabricated flue system shall be warranted against functional failure due to defects in material and manufacturer’s workmanship for a period of 15 years from date of installation.

- The inner diameter of the flue system shall be verified by the manufacturer’s venting computations.  The computations used shall be technically sound and shall incorporate the specific flow characteristics of the inner pipe. The contractor shall furnish the exact operating characteristics of all equipment to the factory representative.

- The manufacturer shall provide “to scale” drawings depicting the actual layout. The prefabricated flue system shall be installed as designed by the manufacturer and in accordance with the terms of the manufacturer’s warranty and in conjunction with sound engineering practices.

# PART-4	PRODUCTS

  - MANUFACTURERS

- Product specification requirements shall be met by using Selkirk Commercial/Industrial Model IPS series exhaust flue or equivalent as approved by the engineer. Equivalent submittals shall specify manufacturer’s model number, and other pertinent identification, and attest that the alternate material is in compliance with all specification requirements.

END OF SECTION 23 51 00 or 23 35 00